| Overview surface centrifugal pump for solar operation flow rate up to 15 m3/h simple installation maintenance-free thanks to brushless DC motor high reliability and life expectancy cost-efficient pumping 2 years manufacturer's warranty against defects in material and workmanship |  | Applications swimming pool water circulation through a filter system and thermal collectors pond management irrigation aquariums etc. |
| --- | --- | --- |

Pump System PS600 BADU Top 12 article # 2921 controller PS 600 motor ECDRIVE 600 BADU Top pump end (PE) BADU Top 12 (manufacturer Speck Pumps) source of energy (not included in delivery) solar generator (340-900 Wp) battery, DC source

Features

| Pump end (PE) BADU Top 12 monoblock-type pump with integrated strainer tank bellow mechanical seal is mounted on a plastic shaft protected sleeve motor/pump shaft has no contact with fluid total electric separation strainer capacity approx. 3 l strainer basket mesh size approx. 3.2 x 2.6 mm Material used for pump end pump casing, strainer basket: PP flange, gland housing: PP TV 40 diffuser: PP TV 40 impeller: PA 66 GF 30 / PC lid: PC, transparent mechanical seal: carbon / ceramic / NBR bolts: steel, galvanized Motor ECDRIVE 600 BADU Top brushless, maintenance-free DC motor |  | Controller PS600 controlling of the pump system and monitoring of the operating states mounted at surface (no submerged electronic parts) two control inputs for well probe (dry running protection), float or pressure switches, remote control etc. automatic reset 20 minutes after well probe turns pump off protected against reverse polarity, overload and high temperature speed control, max. pump speed adjustable to reduce flow rate to approx. 30 % solar operation: integrated MPPT (Maximum Power Point Tracking) battery operation: low voltage disconnect and restart after battery has recovered max. efficiency 92 % (motor + controller) |
| --- | --- | --- |

Technical Data

| PS600 BADU Top12 | Solar Operation | Battery Operation |
| --- | --- | --- |
| max. flow rate [m3/h] | 15 | 13 |
| max. lift [m] | 14 | 13 |
| ambient temperature [oC] | -30 to +45 |
| Controller | PS600 |
| input voltage | solar generator: nominal voltage 48-72 V DC open circuit voltage max. 150 V DC | battery, DC source: nominal voltage 48 V DC |
| type of enclosure | IP 54 |
| dimensions (net/packing) | 395 x 175 x 165 mm / 450 x 250 x 250 mm = 0.027 m3 |
| weight (net/gross) | 4.5 kg / 5.3 kg |
| Motor | ECDRIVE 600 BADU Top |
| max. power input [W] | 600 |
| type of enclosure | IP X4 |
| class of insulation | F |
| Pump End | BADU Top 12 (manufacturer Speck Pumps) |
| suction / max. positive inlet lift | 3.0 m |
| max. casing pressure | 2.5 bar |
| max. water temperature | +60 oC |
| Motor + Pump End | ECDRIVE 600 BADU Top + BADU Top 12 |
| dimensions (net / packing) | see dimension drawing: product information [File temporarily not available] 520 x 220 x 350 mm = 0.0400 m3 |
| weight (net / gross) | 8.7 kg / 9.7 kg |